Planned Potable Water Discharge

San Francisco Bay Municipal Regional Stormwater NPDES Permit (MRP)

Provision C.15.b.iii. (1)

Types of O&M activities:

- Blowoff/hydrant flushing

- Unidirectional hydrant flushing

- Storage tank discharges (maintenance or cleaning operations)

- Valve replacement

New service line installation

Unplanned Potable Water Discharge

San Francisco Bay Municipal Regional Stormwater NPDES Permit (MRP)

Provision C.15.b.iii. (2)

Unplanned discharges are non-routine activities such as:

- Water line breaks

- Leaks

- Overflows

- Fire hydrant shearing

Emergency Flushing

# Text boxes

Final Draft  September 2012

Planned Potable Water Discharge

Discharge all water to sanitary sewer

Use internal operating procedures and BMPs

Use internal operating procedures and BMPs

Discharge water to landscape

Water is entering storm drain or receiving water

Is discharge >250,000 gal/day or >500,000 gallons total?

Notify RWQCB at least 1 week in advance (see Table 1 for notification requirements)

BMPs: Implement appropriate BMPs (Best Management Practices) before discharge.

- Dechlorination

- Erosion/sediment control

Monitor: Collect samples for pH, Turbidity and Chlorine residual at every release after BMPs. (Turbidity can also be monitored in the receiving water)

Compare to Benchmarks: Is Chlorine Residual >0.05 mg/L, Turbidity >50 NTU, pH <6.5 or >8.5? (see Fact Sheet #2 for receiving water background turbidity incremental increase benchmarks.)

Record Data: Record discharge and monitoring data at every discharge (see Table 2)

Report Data: Report data for every discharge in Stormwater Annual Report

If discharge continues, modify BMPs as needed, collect another sample.

Yes

Yes

No

No

Yes

Yes

No

Yes

No

SMCWPPP Water Utility Work Group Fact Sheet #1

SMCWPPP Water Utility Work Group Fact Sheet #1

Unplanned Potable Water Discharge

Record when discharge discovered, notification time inspector arrival and responding crew arrival time.

Use internal operating procedures and BMPs

Discharge entering storm drain or receiving water

Contain the discharge and attain safety of the discharge site.

BMPs: Implement appropriate BMPs

- Administrative

- Dechlorination

- Erosion/sediment control

Monitor: Collect samples for pH, turbidity and chlorine residual, if possible (i.e. if still have discharge after site is secured; may occur during repair activities). Monitoring required at only 10% of unplanned discharges

Compare to Benchmarks: Is Chlorine Residual >0.05 mg/L, Turbidity >50 NTU, pH <6.5 or >8.5?

Record Data: Record response times, discharge and monitoring data at each discharge (see Field Forms)

Report Data: Report data for every discharge in Stormwater Annual Report

If discharge continues, modify BMPs as needed, collect another sample.

Yes

No

Yes

Were there any aquatic impacts (e.g. fish kill) as a result of unplanned discharge?

The discharge might endanger or compromise public health and safety.

Is total volume > 50,000 gallons and chlorine residual   > 0.05 mg/L?

Notify State office of Emergency Services (OES) within 2 hours after becoming aware.

Yes

Notify OES within 2 hours after becoming aware.

Yes

Report (by phone or e-mail) to Water Board Staff no later than 24 hours after becoming aware.

Yes

Within 5 days after initial report submit written report to Water Board staff and interested parties.