## Slide 1: Trash Capture Device Installations
Municipal Maintenance Stormwater Workshop
Kevin McGillicuddy, P.G.
Roscoe Moss Company

## Slide 2: Topics
Large scale screen device design criteria
Installation Examples
Maintenance Practices

## Slide 3: Screen Design Criteria
Site Selection
  Provide adequate access for installation
  and
  future maintenance events

## Slide 4: Screen Design Criteria
Target Flow Calculator
  Peak flow (Q) determined using formula Q = C * I * A
  C = runoff coefficient : 0.8
  I = 1 yr-1 hr rainfall intensity : 0.5 in/hr
  A = tributary drainage area : 150 acres
  Q = Target Flow = : 60.1 cu.ft/sec
  Bypass System Must be Designed to Transfer Flows Above Target Flow Rate

## Slide 5
Overflow Bypass Sections

## Slide 6: Screen Design Criteria
Device Size
  Requires determination of diameter and length
  Diameter: - match outfall dimensions
  - flow line of treated storm event
  Length: - as required to treat target flow with debris in place
  - capacity to hold captured debris between cleaning events

## Slide 7: Screen Configuration Options
Single linear configuration
Parallel multi-screen configuration

## Slide 8: Screen Configuration Options
Single linear configuration
Parallel multi-screen configuration

## Slide 9
City of Antioch
Detention basin area – 6 acres
Drainage area: 200 acres
Target flow: 60 cfs

## Slide 12
30 ft – 42 in dia screen
Treatment capacity 60 cfs up when ¼ full

## Slide 13: Brentwood, CA 15 ft – 48 in screen, treatment capacity 23.4 cfs when ½ full

## Slide 14: Pittsburg, CA 50 ft - 36in screen, treatment capacity 55 cfs when 1/2full

## Slide 15: Milpitas, CA combination radial , semi-circular, and flat panels
30 ft – 42 in screen
Treatment capacity 60 cfs when ½ full

## Slide 19: Maintenance Procedures

## Slide 20
Video

## Slide 21: Questions ?
Please Contact :
Kevin McGillicuddy
Roscoe Moss Company
4360 Worth Street
Los Angeles, CA 90063
Tel: (323) 263-4111
www.roscoemoss.com
Email:kmc@roscoemoss.com